Communication settings:
9600 / 8 / 1 / N

Commands.
Get General Information (0x01)
Request:
Offset	Length	Value	Description
0	2	0x5A 0x5A	Packet header
2	1	0x02	Packet payload size / 2 bytes /
3	1	0x01	Command Id
4	1	0xFD	Checksum

Response:
Offset	Length	Value	Description
0	2	0x5A 0x5A	Packet header
2	1	byte	Packet payload size
3	1	byte	Hardware version/brand ???
4	1	byte	Software version 0x13 = v1.3
5	1	byte	Hour 0x20 = 20h
6	1	byte	Minutes 0x16 = 16m
7	1	byte	Seconds 0x55 = 55s
8	1	byte	Day 0x20 = 20th
9	1	byte	Month 0x01 = January
10	1	byte	Year 0x16 = 2016
11	1	byte	0x00 - STANDBY / 0x01 - AUTO / 0x02 - Timer
12	1	byte	0x00 - CH Priority / 0x01 - DHW Priority / 0x02 - Parallel Pumps / 0x03 - Summer Mode
13	1	byte	0x00 - IDLE / 0x01 - Fan Cleaning / 0x02 - CLEANER / 0x03 - Wait / 0x04 - Loading / 0x05 - HEATING / 0x06 - IGNITION1 / 0x07 - IGNITION2 / 0x08 - UNFOLDING / 0x09 - BURNING / 0x0A - EXTINCTION
14	1	byte
15	1	byte
16	1	Bit 0 / Bit 1 / Bit 2 / Bit 3 / Bit 4 / Bit 5 / Bit 6 / Bit 7	Ignition Fail / Pellet Jam
17	1	byte
18	1	byte
19	1	byte	Tset
20	1	byte	Tboiler
21	1	byte	Tdhw
22	1	byte
23	1	byte	Flame
24	1	Bit 0 / Bit 1 / Bit 2 / Bit 3 / Bit 4 / Bit 5 / Bit 6 / Bit 7	Heater / CH pump / BF / FF
25	1	byte
26	1	byte	Fan
27	1	byte	0x00 - Idle / 0x01 - Suspend / 0x02 - P1 / 0x03 - P2 / 0x04 - P3
28	1	Bit 7	Thermostat (1 - STOP, 0 - NORMAL)
29	1
30	1	byte	Feeder work time in seconds
31	1	byte	Checksum = sum(data) XOR 0xFF

0x02

Set Burner Mode and Priority (0x03)
Request:
Offset	Length	Value	Description
0	2	0x5A 0x5A	Packet header
2	1	0x04	Packet payload size / 4 bytes /
3	1	0x03	Command Id
4	1	byte	Standby - 0x00 / AUTO - 0x01 / Timer - 0x02
5	1	byte	Ch Priority - 0x00 / DHW Priority - 0x01 / Parallel Pumps - 0x02 / Summer Mode - 0x03
6	1	byte	Checksum

Response:

Get Burner Settings (0x04)

0x05

0x06

Set Boiler Temperature (0x07)
Request:
Offset	Length	Value	Description
0	2	0x5A 0x5A	Packet header
2	1	0x03	Packet payload size / 3 bytes /
3	1	0x07	Command Id
4	1	byte	Tboiler
5	1	byte	Checksum

Response:
Offset	Length	Value	Description
0	2	0x5A 0x5A	Packet header
2	1	0x02	Packet payload size / 2 bytes /
3	1	0x34
4	1	0xCA	Checksum

2. Reset feeder counter (0x09)
Request
Offset	Length	Value	Description
0	2	0x5A 0x5A	Packet header
2	1	0x02	Packet payload size / 2 bytes /
3	1	0x09	Command Id
4	1	0xF5	Checksum

Response
Offset	Length	Value	Description
0	2	0x5A 0x5A	Packet header
2	1	0x02	Packet payload size / 2 bytes /
3	1	0x34
4	1	0xCA	Checksum

Case 1 - Burning at Power 2

Pos 13 changed:
0x13 - 0x09 - 0000 1001

Pos 24:
0x1D - 0x08 - 0000 1000

Case 2 - Turn water pump ON
Temperature increased from 53 to 54 and the burner turned the water pump ON.

Pos 13 changed:
0x0A - 0x00 - 0000 0000

Pos 24 changed:
0x15 - 0x00 - 0000 0000
0x1D - 0x08 - 0000 1000

Case 3 - Ignition [Idle -> Fan Cleaning]

Pos 13 changed:
0x0A - 0x00 - 0000 0000
0x0B - 0x01 - 0000 0001

Pos 24 changed:
0x1D - 0x08 - 0000 1000
0x2D - 0x18 - 0001 1000

Pos 26 changed:
0x17 - 0x00 - 0000 0000 - 0
0x7B - 0x64 - 0110 0100 - 100

Pos 28 changed:
0x99 - 0x80 - 1000 0000
0x19 - 0x00 - 0000 0000

Case 4 - Ignition [Fan Cleaning -> Wait]

Pos 13 changed:
0x0B - 0x01 - 0000 0001
0x0D - 0x03 - 0000 0011

Pos 24 changed:
0x2D - 0x18 - 0001 1000
0x1D - 0x08 - 0000 1000

Pos 26 changed:
0x7B - 0x64 - 0110 0100 - 100
0x17 - 0x00 - 0000 0000 - 0

Case 5 - Ignition [Wait -> Loading]

Pos 13 changed:
0x0D - 0x03 - 0000 0011
0x0E - 0x04 - 0000 0100

Pos 24 changed:
0x1D - 0x08 - 0000 1000
0x4D - 0x38 - 0011 1000

Pos 30 changed:
0x1B - 0x00 - 0000 0000
0x1F - 0x04 - 0000 0100

Case 5 - Ignition [Loading -> Ignition1]

Pos 13 changed:
0x0E - 0x04 - 0000 0100
0x10 - 0x06 - 0000 0110

Pos 24 changed:
0x25 - 0x10 - 0001 0000
0x17 - 0x02 - 0000 0010

Pos 26 changed:
0x17 - 0x00 - 0000 0000 - 0
0x3E - 0x27 - 0010 0111 - 39

Case 6 - Ignition [Ignition1 -> Unfolding]

Pos 13 changed:
0x10 - 0x06 - 0000 0110
0x12 - 0x08 - 0000 1000

Pos 24 changed:
0x17 - 0x02 - 0000 0010
0x15 - 0x00 - 0000 0000

Case 7 - Ignition [Unfolding -> Power 2]

Pos 13 changed:
0x12 - 0x08 - 0000 1000
0x13 - 0x09 - 0000 1001

Pos 24 changed:
0x15 - 0x00 - 0000 0000
0x25 - 0x10 - 0001 0000

Pos 27 changed:
0x18 - 0x00 - 0000 0000
0x1B - 0x03 - 0000 0011

Pos 30 changed:
0x1B - 0x00 - 0000 0000
0x1E - 0x03 - 0000 0011

Case 8 - Ignition [Power 2 -> Power 3]

Pos 13:
0x13 - 0x09 - 0000 1001

Pos 24 changed:
0x1D - 0x08 - 0000 1000
0x2D - 0x18 - 0001 1000

Pos 27 changed:
0x1B - 0x03 - 0000 0011
0x1C - 0x04 - 0000 0100

Pos 30 changed:
0x1B - 0x00 - 0000 0000
0x1E - 0x03 - 0000 0011

Case 9 - Ignition [Change water temperature 60℃ -> 59℃]

To 62℃

Date and time

16/12/2016 10:57
0x16	0x14	0x12	0x5A	0x0C
0	1	2	3	4
0x16	0x13	0x10	0x57	0x08

Y	2016 / 16	0x07E0 / 0x10	00 010000
M	12	0x0C	0000 1100
D	16	0x10	000 10000
H	10	0x0A	000 01010
M	57	0x39	00 111001
S	8	0x08	00 001000